## Slide 1: Synchrophasors Magnitude and Phase Steps
Marcelo Britto Martins

## Slide 2: Sampling issues – Generation and Sampling @ 4800Hz
Chart: Phase deviation during 1s
S1 | -0.66999 | -1.5062 | -1.5061 | -1.9865 | -3.0009 | -2.9993 | -3.301 | -4.5026 | -4.5023 | -4.6248
S2 | -0.33736 | -1.5061 | -1.5069 | -1.6591 | -2.9999 | -3.0009 | -3.0172 | -4.4534 | -4.5028 | -4.506
S3 | -0.0084955 | -1.3328 | -1.5068 | -1.507 | -2.6535 | -3.0004 | -3.0009 | -3.9638 | -4.5028 | -4.5025
S4 | -0.0040678 | -1.1952 | -1.5052 | -1.5059 | -2.5166 | -2.9989 | -3.0004 | -3.8302 | -4.5019 | -4.5022
S5 | -0.0015023 | -0.90087 | -1.5061 | -1.5066 | -2.2139 | -3 | -3.0009 | -3.5341 | -4.5034 | -4.5029
S6 | -0.0019303 | -0.6993 | -1.5057 | -1.506 | -2.0213 | -2.9993 | -2.9994 | -3.3346 | -4.5018 | -4.5022
S7 | -0.0032289 | -0.60279 | -1.5061 | -1.5057 | -1.9172 | -2.9998 | -3.0009 | -3.2332 | -4.5034 | -4.5014
S8 | -0.0043573 | -0.52912 | -1.5059 | -1.5063 | -1.8472 | -3.0009 | -3.0002 | -3.1655 | -4.5011 | -4.5023
S9 | -0.0033334 | -0.42251 | -1.5046 | -1.5049 | -1.7456 | -3.0009 | -3.0008 | -3.0612 | -4.5005 | -4.5035
S10 | -0.0029654 | -0.35774 | -1.5068 | -1.5056 | -1.6802 | -3.0005 | -3.0007 | -3.0243 | -4.4753 | -4.502
Chart: Frequency deviation during 1s
S1 | 59.9386 | 60 | 59.9999 | 59.9458 | 60 | 59.9999 | 59.9602 | 60 | 60 | 59.9825
S2 | 59.9574 | 60 | 59.9999 | 59.9785 | 59.9999 | 60 | 59.9978 | 59.9928 | 60 | 59.9996
S3 | 59.9993 | 59.9753 | 60 | 59.9997 | 59.9567 | 59.9998 | 60 | 59.9429 | 60 | 59.9999
S4 | 59.9999 | 59.9597 | 60 | 59.9998 | 59.9456 | 60 | 60 | 59.9384 | 59.9999 | 59.9999
S5 | 59.9999 | 59.9403 | 60 | 59.9999 | 59.9382 | 59.9999 | 60 | 59.9425 | 59.9999 | 60
S6 | 59.9999 | 59.9999 | 59.9999 | 59.9999 | 59.9999 | 59.9999 | 59.9999 | 59.9999 | 59.9999 | 59.9999
S7 | 60 | 59.9403 | 59.9999 | 59.9999 | 59.9509 | 60 | 59.9999 | 59.9678 | 59.9999 | 59.9999
S8 | 60 | 59.9429 | 59.9999 | 59.9998 | 59.9568 | 60 | 59.9999 | 59.9767 | 59.9999 | 60
S9 | 59.9999 | 59.9502 | 59.9999 | 59.9999 | 59.967 | 60 | 60 | 59.9915 | 59.9996 | 60
S10 | 60 | 59.9556 | 59.9999 | 59.9999 | 59.9755 | 60 | 59.9999 | 59.9968 | 59.9961 | 60
Chart: Magnitude deviation during 1s
S1 | 1.0058 | 1.0055 | 1.0055 | 1.0056 | 1.0056 | 1.0056 | 1.0055 | 1.0055 | 1.0055 | 1.0053
S2 | 1.0056 | 1.0056 | 1.0056 | 1.0054 | 1.0056 | 1.0056 | 1.0055 | 1.0053 | 1.0056 | 1.0056
S3 | 1.0056 | 1.0055 | 1.0056 | 1.0056 | 1.0056 | 1.0056 | 1.0056 | 1.0057 | 1.0056 | 1.0056
S4 | 1.0057 | 1.0056 | 1.0056 | 1.0056 | 1.0057 | 1.0056 | 1.0056 | 1.0057 | 1.0056 | 1.0056
S5 | 1.0057 | 1.0058 | 1.0056 | 1.0056 | 1.0058 | 1.0057 | 1.0056 | 1.0058 | 1.0056 | 1.0056
S6 | 1.0057 | 1.0058 | 1.0056 | 1.0056 | 1.0057 | 1.0056 | 1.0057 | 1.0056 | 1.0056 | 1.0056
S7 | 1.0057 | 1.0057 | 1.0056 | 1.0056 | 1.0057 | 1.0057 | 1.0056 | 1.0055 | 1.0056 | 1.0056
S8 | 1.0057 | 1.0057 | 1.0057 | 1.0056 | 1.0056 | 1.0057 | 1.0057 | 1.0055 | 1.0056 | 1.0056
S9 | 1.0057 | 1.0057 | 1.0057 | 1.0057 | 1.0055 | 1.0057 | 1.0057 | 1.0054 | 1.0056 | 1.0056
S10 | 1.0057 | 1.0056 | 1.0057 | 1.0056 | 1.0055 | 1.0057 | 1.0057 | 1.0056 | 1.0054 | 1.0056
Estimation with Steady State Fit
Phase and frequency unstable
Phase drift -4.5 degrees/s

## Slide 3: Sampling issues – Generation @ 14400Hz, Sampling @ 4800Hz – (RA vs CM)
Chart: Phase Deviation: RA x CM
RA1 | -0.28844 | -0.80958 | -1.325 | -1.6638 | -2.1819 | -2.7137 | -3.076 | -3.5566 | -4.0785 | -4.5043
CM1 | -0.30695 | -0.86354 | -1.3884 | -1.7821 | -2.3482 | -2.8804 | -3.2688 | -3.8349 | -4.3669 | -4.7567
Starting phase more stable
Phase drifts linearly -4.5 to -4.75 degrees/s
Frequency low, variation ~ 0.02 Hz
Chart: Frequency
RA4 | 59.9847 | 59.9862 | 59.9867 | 59.9874 | 59.9855 | 59.9859 | 59.9916 | 59.9857 | 59.9853 | 59.9932
CM1 | 59.9837 | 59.9849 | 59.9892 | 59.9851 | 59.9845 | 59.9889 | 59.9841 | 59.9845 | 59.9885 | 59.9847

## Slide 4: Sampling issues – Generation @ 14400Hz, Sampling @ 4800Hz – (RA vs CM)
Chart: Phase Deviation: RA x CM
RA1 | -0.28844 | -0.80958 | -1.325 | -1.6638 | -2.1819 | -2.7137 | -3.076 | -3.5566 | -4.0785 | -4.5043
CM1 | -0.30695 | -0.86354 | -1.3884 | -1.7821 | -2.3482 | -2.8804 | -3.2688 | -3.8349 | -4.3669 | -4.7567
Using CM would sync the generation with sampling
There should not be significant phase or frequency errors and variation
Chart: Frequency
RA4 | 59.9847 | 59.9862 | 59.9867 | 59.9874 | 59.9855 | 59.9859 | 59.9916 | 59.9857 | 59.9853 | 59.9932
CM1 | 59.9837 | 59.9849 | 59.9892 | 59.9851 | 59.9845 | 59.9889 | 59.9841 | 59.9845 | 59.9885 | 59.9847

## Slide 5: Sampling issues – Generation @ 14400Hz, Sampling @ 4800Hz
Generator was taking 4799 or 14399 samples/s - fixed that
Phase drift of 3.3 degrees/s
Chart: Phase drift (degrees)
CM1 | -0.22657 | -0.61575 | -1.0139 | -1.3975 | -1.5931 | -1.9703 | -2.3687 | -2.7583 | -3.0203 | -3.3455

## Slide 6: Sampling issues – Generation @ 48000Hz, Sampling @ 5000Hz
Taking a better generator -> 48000Hz
DVM truncates at 100ns (1/10MHz)
(dt = 1/4800 = 0.028033 s)
Changing dt in the analysis -> phase drift of 3deg/s
Change the sampling frequency to 5000Hz -> dt = 0.02s
Generator 10MHz clock from:
  Atomic clock: phase drift of 0.3 deg/s
  Multimeter clock:
    phase stable, with variations in the order of 0.001 deg (variando na Terceira casa?)
    Frequency stable, with variations in the order of 0.0001 Hz (variando na quarta casa?)
Best configuration:
1 PPS trigger from atomic clock (UTC) for both
Generation at 48000Hz, 10MHz clock from DVM
DVM at 5000Hz, internal 10MHz clock

## Slide 7: Hilbert filter
Estimation of tau for all tests
Simulation vs real data ?
Max error: 2dt
Min error: -1dt

## Slide 8: Phase step - example
Tau = 0.2T, 10deg step
5th window

## Slide 9
1
2
3
4
5
6
7
8
9
Samples

## Slide 11: Phase Steps: Frequency (SS fit vs LM)
Chart: Frequency errors [%], PSp0
LM err [%] | -0.00093334 | -0.009612 | -0.013565 | -0.0063638 | -0.038112 | -0.0043277 | -0.018237 | -0.012217 | -0.0020405
SS err[%] | 0.21061 | 0.42969 | 0.58733 | 0.67126 | 0.71474 | 0.67159 | 0.59468 | 0.43576 | 0.21399
Chart: Frequency errors [%], PSp0
LM err [%] | -0.00093334 | -0.009612 | -0.013565 | -0.0063638 | -0.038112 | -0.0043277 | -0.018237 | -0.012217 | -0.0020405
Chart: Frequency [Hz], PSp0
PS_p_0 | 59.9994 | 59.9942 | 59.9919 | 59.9962 | 59.9771 | 59.9974 | 59.9891 | 59.9927 | 59.9988
LM is more stable and accurate for different step instants (tau)
Uncertainty?
What about other phases?

## Slide 12: Phase Steps: Frequency (SS fit vs LM)
Chart: Estimated Frequency during Phase Step (t5)
SS Freq | 60.0003 | 59.9998 | 59.9999 | 59.9999 | 60.4179 | 60.0004 | 59.9999 | 59.9999 | 59.9999
SS Freq | 60.011
Chart: Estimated Frequency during Phase Step (t5)
SS Freq | 60.0004 | 60.0006 | 60 | 59.9994 | 59.5762 | 60.0004 | 60.0006 | 60 | 59.9995
SS Freq | 59.9779
Chart: Est Frequency, Phase Step (t9)
SS Freq | 60 | 60.0005 | 60.0004 | 59.9997 | 60.1284 | 59.9999 | 60.0003 | 60.0005 | 59.9998
LM Freq | 59.9988
Chart: Est Frequency, Phase Step (t9)
SS Freq | 59.999 | 60.0003 | 60.0004 | 60 | 59.8744 | 60 | 60.0016 | 60.0007 | 59.9997
LM Freq | 59.9987
Frequency:
Steady State:
0.0001 Hz variation
Steps:
SS_fit: 0.5Hz error
LM_fit: 0.05Hz error
LM more stable and accurate during phase step

## Slide 13: Phase Steps: Magnitude (SS fit vs LM)
Chart: Estimated Magnitude during Phase Step (t5)
SS Mag | 0.99618 | 0.99618 | 0.9962 | 0.99623 | 0.992 | 0.99622 | 0.99621 | 0.99625 | 0.99624
LM Mag | 0.99648
Chart: Estimated Mag during Phase Step (t5)
SS Mag | 0.99619 | 0.99619 | 0.99627 | 0.99626 | 0.99889 | 0.99621 | 0.99624 | 0.99627 | 0.99629
LM Mag | 0.99643
Chart: Estimated Mag during Phase Step (t5)
SS Mag | 0.99626 | 0.99629 | 0.99629 | 0.99627 | 0.99317 | 0.99629 | 0.99632 | 0.9963 | 0.99626
LM Mag | 0.99628
Chart: Estimated Mag, Phase Step (t9)
SS Mag | 0.99619 | 0.99623 | 0.99619 | 0.99617 | 0.99586 | 0.99621 | 0.9962 | 0.9962 | 0.99616
LM Mag | 0.99617
Chart: Estimated Mag, Phase Step (t9)
SS Mag | 0.99613 | 0.99618 | 0.9962 | 0.99622 | 0.99681 | 0.99619 | 0.99619 | 0.99621 | 0.9962
LM Mag | 0.99619
LM is more stable and accurate

## Slide 14: Phase Steps: Phase (SS fit vs LM)
Chart: Estimated Phase, Phase Step (t9)
SS Phase_abs | 119.9226 | 119.9199 | 119.9219 | 119.9236 | 120.8254 | 129.9243 | 129.9237 | 129.9219 | 129.9247
LM Phase[deg] | 120.859
Chart: Estimated Phase, Phase Step (t5)
SS | 119.9206 | 119.9229 | 119.9239 | 119.9239 | 124.7393 | 129.9223 | 129.9236 | 129.9246 | 129.924
LM (SS Freq) | 124.9016
Chart: Estimated Phase during Phase Step
SS | 119.922 | 119.9228 | 119.9243 | 119.9232 | 115.0883 | 109.9203 | 109.923 | 109.9245 | 109.9227
LM (SS Freq) | 114.942
Chart: Estimated Phase, Phase Step (t9)
SS Phase_abs | 119.9336 | 119.9205 | 119.9234 | 119.9256 | 118.9976 | 109.9236 | 109.9244 | 109.9242 | 109.9238
LM Phase[deg] | 118.9286
SS and LM have
Good results

## Slide 15: Magnitude Step: Frequency
Frequency estimation in function of step instant
Chart: Estimated Frequency during Mag Step (t5) – MSp0
SS Freq | 60.0004 | 60.0007 | 60.0001 | 59.9995 | 59.9999 | 60.0004 | 60.0006 | 59.9999 | 59.9995
LM Freq | 59.9936
Chart: Frequency errors [%], MSp0
SS err[%] | 0.015381 | 0.02482 | 0.012505 | -0.00094539 | -0.00022013 | 0.00051169 | -0.012496 | -0.023157 | -0.013965
LM err [%] | 0.0066761 | -0.0019535 | -0.0028974 | 0.0069136 | -0.010431 | 0.0074976 | -0.0019976 | -0.0036565 | 0.0078266
Chart: Frequency errors [%], MSp120
SS err[%] | 0.007101 | -0.0080574 | -0.018784 | 0.00082256 | 0.0004957 | -0.003262 | 0.0028979 | 0.010505 | 0.021919
LM err [%] | -0.00092904 | -0.0085405 | 0.0074084 | -0.0066535 | 0.0047619 | 0.0015768 | -0.0060412 | 0.009318 | -0.009904
Chart: Est Frequency, Mag Step (t9)
SS Freq | 60 | 60.0005 | 60.0002 | 59.9999 | 59.9916 | 60.0001 | 60.0003 | 60.0002 | 59.9997
LM Freq | 60.0047
To do:
Compare with simulations
Preliminary results indicate that
LM is more reliable during steps
If so, the generator frequency is not stable during mag step

## Slide 16: Magnitude Step: Magnitude
Chart: Estimated Mag, Mag Step (t9)
SS Mag | 0.90558 | 0.90554 | 0.90552 | 0.90552 | 0.91549 | 0.99616 | 0.99607 | 0.99605 | 0.9961
LM Mag | 0.91427
LM FreqNom | 0.91428
Chart: Estimated Magnitude during Mag Step (t5)
SS | 0.90558 | 0.90559 | 0.90563 | 0.90564 | 0.95056 | 0.99616 | 0.99614 | 0.9962 | 0.9962
LM (SS Freq) | 0.95092
In fact, magnitude and phase of a synchrophasor are always related to the nominal frequency.
If the estimated frequency deviates from the nominal, their estimation is affected.

## Slide 17: Magnitude Step: Phase
Chart: Estimated Phase during Mag Step – t5 MSp0
SS | -0.073411 | -0.076845 | -0.077538 | -0.077302 | -0.073859 | -0.073798 | -0.076049 | -0.078366 | -0.076634
LM (SS Freq) | -0.075511
LM | -0.070115
Chart: Estimated Phase during Mag Step – t5 MSp120
SS | -120.0765 | -120.0769 | -120.0798 | -120.0668 | -120.0778 | -120.0741 | -120.0759 | -120.0766
LM (SS Freq) | -120.0761
LM | -120.0675
Chart: Estimated Phase during Mag Step
SS | 119.9218 | 119.9226 | 119.9252 | 119.9239 | 119.9366 | 119.9219 | 119.9234 | 119.9252 | 119.9242
LM (SS Freq) | 119.9262
LM | 119.9377
Chart: Estimated Phase during Mag Step
SS | -120.0769 | -120.0749 | -120.0768 | -120.0791 | -120.0868 | -120.0762 | -120.0755 | -120.0772 | -120.0781
LM (SS Freq) | -120.0764
LM | -120.0721

## Slide 18: Magnitude Step: Phase
Chart: Estimated Phase, Mag Step (t9)
SS | -0.074889 | -0.074472 | -0.07906 | -0.078931 | -0.12405 | -0.075181 | -0.076746 | -0.078963 | -0.077769
LM | -0.0045808
LM FreqNom | -0.073133
Chart: Estimated Phase, Mag Step (t9)
SS | 119.9214 | 119.9197 | 119.9223 | 119.9243 | 119.9989 | 119.9243 | 119.9218 | 119.9231 | 119.924
LM | 119.8386
LM FreqNom | 119.9204
Chart: Estimated Phase, Mag Step (t9)
SS | -120.0788 | -120.0761 | -120.0747 | -120.0774 | -120.1068 | -120.0778 | -120.0772 | -120.0751 | -120.0792
LM | -120.0762
LM FreqNom | -120.0784
Chart: Estimated Phase, Mag Step (t9)
SS | -0.073699 | -0.07385 | -0.071083 | -0.07427 | -0.029306 | -0.062172 | -0.078393 | -0.078373 | -0.079088
LM | -0.0095536
LM FreqNom | -0.082647
Chart: Estimated Phase, Mag Step (t9)
SS | 119.9318 | 119.9227 | 119.9232 | 119.926 | 119.853 | 119.9268 | 119.9251 | 119.9249 | 119.9336
LM | 119.832
LM FreqNom | 119.9299
Chart: Estimated Phase, Mag Step (t9)
SS | -120.0771 | -120.0769 | -120.0744 | -120.0722 | -120.0493 | -120.0848 | -120.0855 | -120.0693 | -120.0785
LM | -120.0834
LM FreqNom | -120.0846

## Slide 19: Questoes
Variacao de fase com a frequencia nominal: efeito do estimador?
  Nao, esta variacao e esperada, pois para o sincrofasor a fase varia quando a frequencia varia. O que esta variando realmente e a frequencia!
Quais as variações considerando as incertezas?